## Calculator
Exhaust flow rate calculator
4" Exhaust Duct: |  | 6" Exhaust Duct:
Enter velocity pressure in inches of water = |  | Enter velocity pressure in inches of water =
Exhaust flow rate (CFM) = | 0 | Exhaust flow rate (CFM) = | 0
8" Exhaust Duct: |  | 10" Exhaust Duct:
Enter velocity pressure in inches of water = |  | Enter velocity pressure in inches of water =
Exhaust flow rate (CFM) = | 0 | Exhaust flow rate (CFM) = | 0
12" Exhaust Duct:
Enter velocity pressure in inches of water =
Exhaust flow rate (CFM) = | 0

## Conversion Chart
EXHAUST FLOWRATE CONVERSION CHART
Velocity pressure reading corresponding to
specific exhaust duct size (in. of H2O)
Flowrate (CFM) | 4" | 6" | 8" | 10" | 12"
50 | 0.020592 | 0.0040572 | 0.0012796 | 0.00052474 | 0.00025293
100 | 0.082368 | 0.016229 | 0.0051185 | 0.0020989 | 0.0010117
150 | 0.18533 | 0.036514 | 0.011517 | 0.0047226 | 0.0022763
200 | 0.32947 | 0.064915 | 0.020474 | 0.0083958 | 0.0040468
250 | 0.5148 | 0.10143 | 0.031991 | 0.013118 | 0.0063232
300 | 0.74131 | 0.14606 | 0.046067 | 0.018891 | 0.0091054
350 | 1.009 | 0.1988 | 0.062702 | 0.025712 | 0.012393
400 | 1.3179 | 0.25966 | 0.081896 | 0.033583 | 0.016187
450 | 1.6679 | 0.32863 | 0.10365 | 0.042504 | 0.020487
500 | 2.0592 | 0.40572 | 0.12796 | 0.052474 | 0.025293
550 | 2.4916 | 0.49092 | 0.15484 | 0.063493 | 0.030604
600 | 2.9652 | 0.58423 | 0.18427 | 0.075562 | 0.036422
650 | 3.48 | 0.68566 | 0.21626 | 0.088681 | 0.042745
700 | 4.036 | 0.7952 | 0.25081 | 0.10285 | 0.049574
750 | 4.6332 | 0.91286 | 0.28792 | 0.11807 | 0.056909
800 | 5.2715 | 1.0386 | 0.32759 | 0.13433 | 0.064749
850 | 5.9511 | 1.1725 | 0.36981 | 0.15165 | 0.073096
900 | 6.6718 | 1.3145 | 0.4146 | 0.17001 | 0.081948
950 | 7.4337 | 1.4646 | 0.46195 | 0.18943 | 0.091307
1000 | 8.2368 | 1.6229 | 0.51185 | 0.20989 | 0.10117